## framework
1.Communication rules Communication type: Half duplex asynchronous serial communication Baud rate: 19200BPS Data bit: 8BIT, low start Parity check: EVEN Start bit: 1BIT (Low level) End bit: 1BIT(High level)
Reserved： PCB self-adapting to below baud rate:1200、2400、4800、9600、19200； PCB self-adapting to below data type: None Parity check 1 stop bit/Odd Parity check 1 stop bit/Even Parity check 1 stop bit PCB self-checking if not finished in 5~34 seconds after powered, unit use standard setting stored in EEPROM file.
2.Communication protocol: MODBUS RTU protocol 2.1、General discription System structure: User interface (controller): Master Indoor unit: 1# slave (device address:01) Outdoor unit: 2# slave (device address:02) User interface works as the master and has dominating command authority. The master timely checks parameters and data from the slaves and makes command in time. The slave unit, as the execution unit, will work as the master’s command; meanwhile the slave is able to do self-checking and correct errors by itself. For example: If the master did not send communication request timely, the slave will generate communication error failure code and response with corresponding protection action, such as stop heat pump work and etc.
2.2、Function code and data definition 2.2.1、Function code defination (The detailed definition please refers to MODBUS protocol related regulations.)In this protocol, 3 function codes are used, their description is as following:
Function code =03: Reading from multiple save registers. The master requests to read more than one 8-bit-binary data from the salve. Data format shown as below:
Master(request) | Slave (response)
Device address | Unit address
Function code(03) | Function code (03)
Register start address high bit | Data length
Register start address low bit | Data 1 high bit
Register quantity high bit | Data 1 low bit
Register quantity low bit | :
CRC parity low bit | :
CRC parity high bit | Data N high bit
Data N low bit
CRC parity low bit
CRC parity high bit
Function code =06H: Writing to single register. The master sends two 8-bit-binary data to the slave. Data format shown as below:
Master(request) | Slave (response)
Device address | Unit address
Function code(06) | Function code (06)
Register start address high bit | Register start address high bit
Register start address low bit | Register start address low bit
Data high bit | Data high bit
Data low bit | Data low bit
CRC parity low bit | CRC parity low bit
CRC parity high bit | CRC parity high bit
Function code =16: Writing to multiple registers. The master sends multiple 8-bit-binary data to the slave. Data format shown as below:
Master(request) | Slave (response)
Device address (01) | Unit address (01)
Function code (16) | Function code (16)
Register start address high bit | Register start address high bit
Register start address low bit | Register start address low bit
Number of register high bit | Number of register high bit
Number of register low bit | Number of register low bit
Data length | CRC parity low bit
Data 1 high bit | CRC parity high bit
Data 1 low bit
:
:
Data N high bit
Data N low bit
CRC parity low bit
CRC parity high bit
Function code=21: reserve(write) several registers. Master unit send binary to slave unit.
Master(request) | Slave (response)
Device address (01) | Device address (01)
Function code（21） | Function code（21）
Index of packet high bit | Index of packet high bit
Index of packet low bit | Index of packet low bit
Communication stop icon | Communication stop icon
0：on，1：off
Communication write situation | Communication write situation
0：Not write，1：wrote | 0：Not write，1：wrote
Data length（128） | Data length
Date 1 | CRC parity low bit
Date 2 | CRC parity high bit
：
：
Date 127 bit
Date 128 bit
CRC parity low bit
CRC parity high bi
3、MODBUS Function Conventions: 3.1、MODBUS function code 03 and function code 16 can write/read at any register position if the action is within current definition range. But if the action exceeds the range of current definition, the slave would not response to master. It is suggested to write/read EEPROM in a whole. 3.2、The definition of MODBUS registers: 10 registers will be uniformly defined in integer. Not defined registers are seen as reserved, with value as 0 for all.

## 1000
running data setting(mode/temp. setting, function)
Address | Function code | content | Byte length | Function description | 功能说明
1000 | 03/06/16 | set mode | double byte | 0--Standby mode; 1--Hot water mode; 2--Heating mode; 3--Cooling mode; 4--Auto mode; 5--Hot water + Heating mode; 6--Hot water + Cooling mode; 7--Hot water + Auto mode; | 机组运行模式
1001 | 03/06/16 | Reserved | double byte | Reserved
1002 | 03/06/16 | Reserved | double byte | Reserved
1003 | 03/06/16 | ∆T Compressor Speed-reduction | double byte | Value =2-10℃ | 到温降频回差设定值
1004 | 03/06/16 | Cooling Anti-freeze deviation temp. | double byte | value=0-5 | 制冷蒸发温度防冻偏移值，板换默认为0
1005 | 03/06/16 | Reserved | double byte | Reserved
1006 | 03/06/16 | Maximum operating temperature of heat pump | double byte | Value =50-60℃ | 压缩机允许运行的最高出水温度
1007 | 03/06/16 | Minimum operating temperature of the heat pump | double byte | Value =3-10℃ | 压缩机允许运行的最低出水温度
1008 | 03/06/16 | External Signal Control | double byte | 0：Invalid； 1：valid； | 外部远程开关信号
1009 | 03/06/16 | Water flow switch valid | double byte | 0：Invalid 1~60：Effective value is the checking water flow switching time (seconds) | 水流开关功能设置
1010 | 03/06/16 | Reserved | double byte | Reserved
1011 | 03/06/16 | Reserved | double byte | Reserved
1012 | 03/06/16 | Working type of circulating water pump | double byte | 0：ID control； 1--15：After setting, change for 0 automatically (auto mode)； 16： Constantly working | 水泵排空功能
1013 | 03/06/16 | Reserved | double byte | Reserved
1014 | 03/06/16 | Reserved | double byte | Reserved
1015 | 03/06/16 | Low noise mode selection of heat pump | double byte | 0：Off； 1：On； | 风速按E方设定值，频率≤F7运行
1016 | 03/06/16 | Circulation pump Stop N minutes and work 1 minute | double byte | 0：Off 1-15：Function valid,Stop time(minute) | 水泵在机组到温停机时的运行方式
1017 | 03/06/16 | Low frequency F1 operation duration | double byte | Value =10-60(minute) | 允许机组低频运行的最长时间设定
1018 | 03/06/16 | Anti-Legionella Function | double byte | 0：Off； 1：On；
1019 | 03/06/16 | Anti-Legionella setting temperature | double byte | Value =60-75℃
1020 | 03/06/16 | Anti-Legionella duration | double byte | Value =10-60(minute)
1021 | 03/06/16 | The longest allowed Anti-Legionella working time | double byte | Value =10-240(minute)
1022 | 03/06/16 | Anti-freezing function valid | double byte | 0：Invalid； 1：valid | 待机防冻功能是否有效
1023 | 03/06/16 | Ambient Temp. to Activate First Class Anti-freezing | double byte | Value =5-10℃ | 一级防冻与二级防冻的进入与退出点 一级防冻：只运行水泵进行防冻； 二级防冻：压缩机系统启动加热；
1024 | 03/06/16 | Ambient Temp. to Activate Second Class Anti-freezing | double byte | Value =0-4℃
1025 | 03/06/16 | Ambient Temp. to Stop Second Class Anti-freezing | double byte | Value =0-10℃
1026 | 03/06/16 | Water Temp. to Activate Second Class Anti-freezing | double byte | Value =0-30℃
1027 | 03/06/16 | Water Temp. to Stop Second Class Anti-freezing | double byte | Value =0-30℃
1028 | 03/06/16 | DHW mode valid | double byte | 0：Invalid； 1：valid | 热水功能选择
1029 | 03/06/16 | Heating mode valid | double byte | 0：Invalid； 1：valid | 制热功能选择
1030 | 03/06/16 | Cooling mode valid | double byte | 0：Invalid； 1：valid | 制冷功能选择
1031-39 | 03/06/16 | Reserved | double byte | Reserved
1040 | 03/06/16 | Setpoint DHW | double byte | Value =25-75℃ | 热水设定温度
1041 | 03/06/16 | DHW Restart ∆T Setting | double byte | Value =0-10℃ | 热水再启动回差
1042 | 03/06/16 | Reserved | double byte | Reserved
1043 | 03/06/16 | Reserved | double byte | Reserved
1044 | 03/06/16 | Reserved | double byte | Reserved
1045 | 03/06/16 | Sanitary water rising 1℃ cycle, judge the hot water capacity. | double byte | Value =1-120(minute) | 热水升温速率判断
1046 | 03/06/16 | Sanitary water min. working time for Shifting Priority | double byte | Value =20-180(minute) | 采暖平衡时的热水最小运行时间
1047 | 03/06/16 | Reserved | double byte | Reserved
1048 | 03/06/16 | Reserved | double byte | Reserved
1049 | 03/06/16 | Reserved | double byte | Reserved
1050 | 03/06/16 | Backup heat source function | double byte | 0：Invalid； 1：valid;
1051 | 03/06/16 | The ambient temperature judgment point 1 of backup heat source operating | double byte | Value = T *100 +3000 (T=-30℃~45℃) ex. 5500 = 25.00 (℃)*100 +3000
1052 | 03/06/16 | The ambient temperature judgment point 2 of backup heat source operating (larger than the point 1) | double byte | Value = T *100 +3000 (T=-30℃~45℃) ex. 5500 = 25.00 (℃)*100 +3000
1053 | 03/06/16 | Cooling curve on or off | double byte | 0：off； 1：on;
1054 | 03/06/16 | Cooling Curve Ambient Temperature 1 | double byte | Value =0-45℃
1055 | 03/06/16 | Cooling Curve Water Temperature /Ambient Temperature 1 | double byte | Value =7-25℃
1056 | 03/06/16 | Cooling Curve Ambient Temperature 2 (larger than ambient temperature 1) | double byte | Value =0-45℃
1057 | 03/06/16 | Cooling Curve Water Temperature /Ambient Temperature 2 | double byte | Value =7-25℃
1058 | 03/06/16 | Cooling Curve Ambient Temperature 3 (larger than ambient temperature 2) | double byte | Value =0-45℃
1059 | 03/06/16 | Cooling Curve Water Temperature /Ambient Temperature 3 | double byte | Value =7-25℃
1060 | 03/06/16 | Setting temperature for heating | double byte | Value =25-75℃ | 制热设定温度
1061 | 03/06/16 | Heating Restart ∆T Setting | double byte | Value =0-10℃ | 制热再启动回差
1062 | 03/06/16 | Dual-mode heating priority | double byte | 0：DHW priority； 1：Heating priority | 热水+制热双模式下的优选级选择
1063 | 03/06/16 | Auto Mode of heating mode activation ambient temperature | double byte | Value = T *100 +3000 (T=-10℃~20℃) ex. 5500 = 25.00 (℃)*100 +3000
1064 | 03/06/16 | Heating maximum temp. | double byte | 0：Invalid, >0Set the maximum working temperature of heating Value =0 or 42-65℃ | 制热曲线功能设定温度的上限值
1065 | 03/06/16 | Heating emergency start | double byte | 0：Invalid； 1：valid； | 制热应急功能，除霜出水过低保护后，电加热开启
1066 | 03/06/16 | Reserved | double byte | Reserved
1067 | 03/06/16 | Reserved | double byte | Reserved
1068 | 03/06/16 | Reserved | double byte | Reserved
1069 | 03/06/16 | Heating electric heater start value | double byte | 0-250(minute*degree) | 制热水温在每分钟内的温差积分目标值
1070 | 03/06/16 | Reserved | double byte | Reserved
1071 | 03/06/16 | Reserved | double byte | Reserved
1072 | 03/06/16 | Three-way valve heating end configuration | double byte | 0：Share with the DHW end； 1：Share with the cooling end； | 设置采暖水路系统是热水一路，还是与制冷一路
1073 | 03/06/16 | Shifting Priority Stating Temp. | double byte | Value = T *100 +3000 (T=-15℃~15℃) ex. 5500 = 25.00 (℃)*100 +3000 Value =-29 or -15℃~15℃ -29--Shifting Priority Invalid. | 采暖平衡启动开启与开启的设定温度
1074 | 03/06/16 | Reserved | double byte | Reserved
1075 | 03/06/16 | Shifting Priority heating delta T | double byte | Value =3-20℃ | 采暖平衡的制热回差设定
1076 | 03/06/16 | Heating maximum working time for Shifting Priority | double byte | Value =20-180(Second) | 采暖平衡的制热最长运行时间设定
1077 | 03/06/16 | Reserved | double byte | Reserved
1078 | 03/06/16 | Heating Curve | double byte | 0：Invalid； 1：valid； | 制热曲线功能
1079 | 03/06/16 | Reserved | double byte | Reserved
1080 | 03/06/16 | Heating curve point 1 ambient temperature | double byte | Value = T *100 +3000 (T=-20℃~45℃) ex. 5500 = 25.00 (℃)*100 +3000 | 曲线A点的环温与水温值
1081 | 03/06/16 | Heating curve point 1 sets water temperature | double byte | Value =20-65℃
1082 | 03/06/16 | Heating curve point 2 ambient temperature ( >Heating curve point 1 ambient temperature) | double byte | Value = T *100 +3000 (T=-20℃~45℃) ex. 5500 = 25.00 (℃)*100 +3000 | 曲线B点的环温与水温值
1083 | 03/06/16 | Heating curve point 2 sets water temperature | double byte | Value =20-65℃
1084 | 03/06/16 | Heating curve point 3 ambient temperature ( >Heating curve point 2 ambient temperature) | double byte | Value = T *100 +3000 (T=-20℃~45℃) ex. 5500 = 25.00 (℃)*100 +3000 | 曲线C点的环温与水温值
1085 | 03/06/16 | Heating curve point 3 sets water temperature | double byte | Value =20-65℃
1086 | 03/06/16 | Heating curve point 4 ambient temperature ( >Heating curve point 3 ambient temperature) | double byte | Value = T *100 +3000 (T=-20℃~45℃) ex. 5500 = 25.00 (℃)*100 +3000 | 曲线D点的环温与水温值
1087 | 03/06/16 | Heating curve point 4 sets water temperature | double byte | Value =20-65℃
1088 | 03/06/16 | Heating curve point 5 ambient temperature ( >Heating curve point 4 ambient temperature) | double byte | Value = T *100 +3000 (T= -20℃~45℃) ex. 5500 = 25.00 (℃)*100 +3000 | 曲线E点的环温与水温值
1089 | 03/06/16 | Heating curve point 5 sets water temperature | double byte | Value =20-65℃
1090 | 03/06/16 | Cooling setting temperature | double byte | Value =7-25℃ | 制冷设定温度
1091 | 03/06/16 | Cooling Restart ∆T Setting | double byte | Value =0-10℃ | 制冷再启动回差
1092 | 03/06/16 | Auto Mode of cooling mode activation ambient temperature | double byte | Value =21-35℃
1093 | 03/06/16 | Reserved | double byte | Reserved
1094 | 03/06/16 | Reserved | double byte | Reserved
1095 | 03/06/16 | Reserved | double byte | Reserved
1096-99 | 03/06/16 | Reserved | double byte | Reserved

## 1200
water system running datas
Address | Function code | content | Byte length | Function description | 功能说明
1200 | /03 | Outdoor ambient temp. (Ta) | double byte | Value = T *100 +3000 (T= -20℃~75℃) ex. 5500 = 25.00 (℃)*100 +3000 | 室外环境温度
1201 | /03 | DHW Temp.(TW) | double byte | Value = T *100 +3000 (T= -20℃~75℃) ex. 5500 = 25.00 (℃)*100 +3000 | 热水温度
1202 | /03 | Cooling water temp.(TH) | double byte | Value = T *100 +3000 (T= -20℃~75℃) ex. 5500 = 25.00 (℃)*100 +3000 | 制冷温度，由出水温度的影射
1203 | /03 | Outlet water temp. | double byte | Value = T *100 +3000 (T= -20℃~75℃) ex. 5500 = 25.00 (℃)*100 +3000 | 出水温度
1204 | /03 | Inlet water temp. | double byte | Value = T *100 +3000 (T= -20℃~75℃) ex. 5500 = 25.00 (℃)*100 +3000 | 进水温度
1205 | /03 | Inner coil temp. | double byte | Value = T *100 +3000 (T= -20℃~75℃) ex. 5500 = 25.00 (℃)*100 +3000 | 内盘管温度
1206 | /03 | Heating water temp. | double byte | Value = T *100 +3000 (T= -20℃~75℃) ex. 5500 = 25.00 (℃)*100 +3000 | 制热温度，由出水温度的影射
1207 | /03 | Reserved | double byte | Reserved
1208 | /03 | Reserved | double byte | Reserved
1209 | /03 | Reserved | double byte | Reserved
1210 | /03 | Reserved | double byte | Reserved
1211 | /03 | Reserved | double byte | Reserved
1212 | /03 | Interlock switch | double byte | 0：OFF； 1：ON；
1213 | /03 | Water flow switch | double byte | 0：OFF； 1：ON； | 水流开关状态
1214 | /03 | Reserved | double byte | Reserved
1215 | /03 | Reserved | double byte | Reserved
1216 | /03 | Reserved | double byte | Reserved
1217 | /03 | Reserved | double byte | Reserved
1218 | /03 | Reserved | double byte | Reserved
1219 | /03 | Reserved | double byte | Reserved
1220 | /03 | Reserved | double byte | Reserved
1221 | /03 | Reserved | double byte | Reserved
1222 | /03 | Reserved | double byte | Reserved
1223 | /03 | Reserved | double byte | Reserved
1224 | /03 | Reserved | double byte | Reserved
1225 | /03 | Reserved | double byte | Reserved
1226 | /03 | Failure 1 | double byte | BIT0：Ambient temp. sensor failure BIT1：DHW temp. sensor failure BIT2：Reserved BIT3：Outlet temp. sensor failure BIT4：Water temp. sensor failure BIT5：Inner coil temp. sensor failure BIT6：Reserved BIT7：Reserved BIT8：Reserved BIT9：Reserved BIT10：Reserved BIT11：Reserved BIT12：Reserved BIT13：Water flow protection failure BIT14：EEPROM Failure BIT15：Reserved | 水系统故障列表
1227 | /03 | Protection | double byte | BIT0：Reserved BIT1：Reserved BIT2：Reserved BIT3：Reserved BIT4：Reserved BIT5：Reserved BIT6：Cooling coil anti-freezing protection BIT7：Reserved BIT8：Water flow protection BIT9：Cooling water temp. too low (Tuo) BIT10：Water outlet temp. too high (Tuo) BIT11：During defrosting, the water temperature is too low protection BIT12：Reserved BIT13：First class anti-freezing protection BIT14：Secondary anti-freezing protection BIT15：Reserved | 水系统保护列表
1228 | /03 | Reserved | double byte | Reserved
1229 | /03 | Reserved | double byte | Reserved
1230 | /03 | Reserved | double byte | Reserved
1231 | /03 | Three-way valve status (in cooling) | double byte | 0：Off； 1：Open； | 三通阀制冷端状态
1232 | /03 | Three-way valve status (in DHW) | double byte | 0：Off； 1：Open； | 三通阀热水端状态
1233 | /03 | Reserved | double byte | Reserved
1234 | /03 | Status of relay for auxiliary electric heating | double byte | 0：Off； 1：Open； | 辅助电加热状态
1235 | /03 | Reserved | double byte | Reserved
1236 | /03 | Reserved | double byte | Reserved
1237 | /03 | Reserved | double byte | Reserved
1238 | /03 | Circulating pump control relay status | double byte | 0：Off； 1：Open； | 水泵状态
1239 | /03 | Reserved | double byte | Reserved
1240 | /03 | Reserved | double byte | Reserved
1241 | /03 | DHW running state | double byte | 0：Not running； 1：DHW is running； | 热水模式运行状态
1242 | /03 | Heating running state | double byte | 0：Not running； 1：Heating is running； | 制热模式运行状态
1243 | /03 | Cooling running state | double byte | 0：Not running； 1：Cooling is running； | 制冷模式运行状态
1244-49 | /03 | Reserved | double byte | Reserved

## 5100
refrigerant system running datas
Address | Function code | content | Byte length | Function description | 功能说明
5100 | /03 | Current operation mode | Double byte | BIT2~BIT0： 000：Standby mode 001：Cooling mode 010：Heating mode 011：Hot water mode 100：Forced defrosting mode 101：EEPROM data writing 110： Inspection (Reserved) 111：Reserved | 外机运行模式（待机、制冷、制热）
5101 | /03 | AC input voltage (RMS) | Double byte | Value： 0-300 (0-300V) | 单相输入电压/三相的平均单相电压
5102 | /03 | AC input current (RMS) | Double byte | Value：0-500 ( 0-50A) | 单相输入电流/三相的平均单相电流
5103 | /03 | Compressor frequency limit at current time (Smaller or equal to current setting value) | double byte | Value：0-120 ( HZ) | 压缩机限频频率（保护限制）
5104 | /03 | Compressor running speed | double byte | Value：0-120 ( HZ) | 压缩机实际运行频率
5105 | /03 | DC fan speed limited speed ( may not equal to current setting value) | double byte | Value：0 – 2000（RPM） | DC风机转速限频值（保护限制）
5106 | /03 | DC fan 1 running speed | double byte | Value： 0 – 2000（RPM） | DC风机1实际反馈转速
5107 | /03 | DC fan 2 running speed | double byte | Value： 0 – 2000（RPM） | DC风机2实际反馈转速（单风机时，不显示）
5108 | /03 | EEV steps | double byte | Value： 0 – 500（P） | EEV膨胀阀开度
5109 | /03 | Relay feedback | double byte | 0：OFF 1：ON BIT0：Reserved BIT1：Auxiliary electric heating relay BIT2： Bottom plate heater BIT3：Compressor crankcase heater BIT4：Reserved BIT5：Reserved BIT6：4-way valve BIT7：Circulating pump relay BIT8：3-way valve relay BIT9-Bit15：Reserved | 继电器负载输出标记位
5110 | /03 | EVI steps | double byte | Value： 0 – 500（P） | EVI膨胀阀开度
5111 | /03 | Outdoor ambient temp.(Ta) | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. 5500 = 25.00 (℃)*100 +3000 | 环境温度显示值
5112 | /03 | Outdoor evaporator coil temp. (Tp) | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. 5500 = 25.00 (℃)*100 +3000 | 外盘管温度显示值
5113 | /03 | Outdoor gas discharge temp.(Td) | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. 5500 = 25.00 (℃)*100 +3000 | 排气温度显示值
5114 | /03 | Outdoor gas return temp.(Ts) | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. 5500 = 25.00 (℃)*100 +3000 | 回气温度显示值
5115 | /03 | Compressor code | double byte | EX. 0 or 3584~3599 | 压缩机识别码
5116 | /03 | Outdoor unit dip-switch | double byte | BIT0: Unit address 0(dip-switch4) BIT1: Unit address 1(dip-switch3) BIT2: Unit address 2(dip-switch2) BIT3: Unit address 3(dip-switch1) BIT4: Reserved BIT5: Reserved BIT6: Reserved BIT7: Reserved BIT8: Reserved BIT9: Reserved BIT10: Reserved BIT11：low pressure switch 0：OFF 1：ON BIT12：high pressure switch 0：OFF 1：ON Bit13-Bit15：Reserved | 开关量状态显示
5117 | /03 | Evaporator pressure （Low pressure） | double byte | Value:0-600(0-60Bar) | 压低压力值显示
5118 | /03 | Condenser pressure （High pressure） | double byte | Value:0-600(0-60Bar) | 高压压力值显示
5119 | /03 | Defrosting entering signal | double byte | 0：not defrosting 1：defrosting | 除霜状态显示
5120 | /03 | Failure protection 1 (protection sort) | double byte | BIT0：Main line current protection BIT1：Compressor phase current protection BIT2：IPM module protection BIT3：Compressor oil return protection BIT4：High Pressure switch protection BIT5：Compressor speed down caused by too high pressure detected by pressure sensor BIT6：1st start pre-heat protection BIT7：Outdoor gas discharge temp.sensor protection BIT8：Outdoor evaporator coil temp.sensor protection BIT9：AC high/low voltage protection BIT10：Failure caused by ambient Temp. BIT11：Frequency limit protection by ambient Temp. BIT12：Low pressure switch protection BIT13：Compressor speed down caused by too low pressure detected by low pressure sensor BIT14~BIT15：Reserved | 保护类标记位
5121 | /03 | Failure protection 2 (sensor failure sort) | double byte | BIT0：Outdoor ambient temp. sensor failure BIT1：Outdoor evaporator coil temp.Sensor failure BIT2：Outdoor gas discharge temp. sensor failure BIT3：Outdoor gas return temp. sensor failure BIT4：Evaporator pressure sensor failure BIT5：Condenser pressure sensor failure BIT6：High pressure switch lock protection BIT7：Low pressure switch lock protection BIT8：DC fan A failure BIT9：DC fan B failure BIT10：Evaporating pressure lock protection BIT11：Condenser pressure lock protection BIT12~BIT15：Reserved | 硬件故障类标记位
5122 | /03 | Failure protection 3 (system failure sort) | double byte | Bit0：Master and slave communication failure Bit1：Outdoor main control PCB and module communication failure Bit2：Compressor phase current failure (open/short circuit) Bit3：Compressor phase current overload (over current) Bit4：Compressor driver failure Bit5：Module VDC over high/low voltage failure Bit6：AC current failure Bit7：EEPROM failure Bit8~Bit15：Reserved | 系统故障类标记位
5123 | /03 | Outdoor unit PCB program version | double byte | bit15 – bit8 : software version Number Main code bit7 – bit0 : Software version number slave code Ex：0x0102：V001_T02 | 主控板软件版本号
5124 | /03 | Outdoor unit PCB EEPROM program version | double byte | 114 | 主控板E方版本号
5125 | /03 | Reserved | double byte | Reserved
5126 | /03 | Reserved | double byte | Reserved
5127 | /03 | Reserved | double byte | Reserved
5128 | /03 | Main control board item No. | double byte | Value：0x0000-0xFFFF：Item No. Ex：0x0030：AC00I30 | 主控板项目号
5129 | /03 | Outlet temperature of Economizer（for EVI model） | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. 5500 = 25.00 (℃)*100 +3000 | EVI系统的经济器的进出口温度与压力
5130 | /03 | Inlet temperature of Economizer（for EVI model） | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. 5500 = 25.00 (℃)*100 +3000
5131 | /03 | EVI pressure sensor (Reserved) | double byte | Value:0-600(0-60Bar)
5132 | /03 | Condensing temperature (high pressure corresponds to saturation temperature) | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. -1000= -40.00 (℃)*100 +3000 | 冷凝温度（室外机跟据高压压力换算的饱和温度）
5133 | /03 | Evaporating temperature (low pressure corresponds to saturation temperature) | double byte | Value = T *100 +3000 (T= -30℃~100℃) ex. -1000= -40.00 (℃)*100 +3000 | 蒸发温度（室外机跟据低压压力换算的饱和温度）
5134-5140 | /03 | Reserved | Reserved | Reserved

## 1800
PARAMETER MODIFICATION（1000/3000 MODIFICATION）
Address | Function code | content | Byte length | Function description | 功能说明
1800 | 03/06/16 | EEPROM Burning instructions | double byte | 0：Do not start burning EEPROM 1：Start indoor unit part EEPROM burning 2：Start outdoor unit part EEPROM burning | 用于更新1000地址与3000地址参数值时使用 ，每修改一次参数，都需要执行一次保存，主板才会生效； 0表示不进行参数保存 当设置为1时，保存1000地址段的当前设定值； 当设置为2时，保存3000地址段的当前设定值；
1801 | 03/06/16 | EEPROM burning state | double byte | 0：Nothing 1：The burning state of indoor unit part EEPROM 2：The burning state of outdoor unit part EEPROM | 参数保存的标记位显示，当参数在保存过程中，对应的值显示 显示0：表示没有保存操作 显示1：表示正在保存1000地址段参数； 显示2：表示正在保存3000地址段参数；

## 10000
485 update software address
Address | Function code | content | Byte length | Function description | 功能说明
10000 | 03/6/16 | Current order | double byte | 0.Standby 1.Burn 2.Run App model | 此部分地址，只用于485远程更新程序使用，具体操作说明，请查看更新程序的指导原码
10001 | 03/6/16 | state | double byte | 0//Standby 1//Erase FLASH 2//Burn FLASH 3//Transmission file 4//verify
10002 | 03/6/16 | fault protection | double byte | 0.No failure 1.verify FLASH failed 2.communication failure 3.Write FLASH failed.
10003 | 03/6/16 | Index of protocol | double byte | 128K Maximum FLASH
10004 | 03/6/16 | reserved | double byte | reserved